## Sheet1
name | dataType | documentation | engUnit | valueSource | opcItemPath | tagType | alarmMode | alarmName | historyEnabled | historySampleRate | historySampleRateUnits | shortDescription | stateLabels | stateValues
BATT_V | Int2 | Battery Voltage | V | opc | ns=1;s=[{Device}]HR61 | AtomicTag | [5 empty] | Battery Voltage
CLNT_TEMP | Int2 | Coolant Temperature | °F | opc | ns=1;s=[{Device}]HR64 | AtomicTag | [5 empty] | Coolant Temperature
CMN_ALM | Int2 | Common Alarm |  | opc | ns=1;s=[{Device}]HR561 | AtomicTag | WhenTrue | Alarm |  |  |  | Common Alarm | Normal¦Alarm | 0¦1
CMN_SHTDN | Int2 | Common Shutdown |  | opc | ns=1;s=[{Device}]HR400.13 | AtomicTag | WhenTrue | Alarm |  |  |  | Common Shutdown | Normal¦Alarm | 0¦1
COMM_FAIL | Int2 | Communications Failure |  | opc | ns=1;s=[{Device}]HR231 | AtomicTag | WhenTrue | Alarm |  |  |  | Communications Failure | Inactive¦Active¦Failed | 0¦1¦2
CTRL_SW_POS | Int2 | Control Switch Position |  | opc | ns=1;s=[{Device}]HR10 | AtomicTag | WhenTrue | Alarm |  |  |  | Control Switch Position | Off¦Manual¦Auto | 0¦1¦2
RUPT_BASIN_SW | Int2 | Rupture Basin Switch |  | opc | ns=1;s=[{Device}]HR516 | AtomicTag | WhenTrue | Alarm |  |  |  | Rupture Basin Switch | Normal¦Alarm | 0¦1
E_STOP | Int2 | Emergency Stop |  | opc | ns=1;s=[{Device}]HR512 | AtomicTag | WhenTrue | Alarm |  |  |  | Emergency Stop | Normal¦Alarm | 0¦1
ENG_RT | Int4 | Engine Runtime | hrs | opc | ns=1;s=[{Device}]HR71 | AtomicTag | [5 empty] | Engine Runtime
ENG_SPD_RPM | Int2 | Engine Speed RPM | rpm | opc | ns=1;s=[{Device}]HR68 | AtomicTag |  |  | TRUE | 5 | MIN | Engine Speed RPM
FAIL_TO_STRT | Int2 | Failed to Start |  | opc | ns=1;s=[{Device}]HR400.1 | AtomicTag | WhenTrue | Alarm |  |  |  | Failed to Start | Normal¦Alarm | 0¦1
FREQ | Int4 | Frequency |  | opc | ns=1;s=[{Device}]HR145 | AtomicTag | [5 empty] | Frequency
GEN_STRT_CMD | Int2 | Generator Start Command |  | opc | ns=1;s=[{Device}]HR283 | AtomicTag | [5 empty] | Generator Start Command
GEN_ZR | Int2 | Generator Run |  | opc | ns=1;s=[{Device}]HR283 | AtomicTag | [5 empty] | Generator Run
GENSET_LOAD | Int4 | Genset Load |  | opc | ns=1;s=[{Device}]HR2002 | AtomicTag |  |  | TRUE | 5 | MIN | Genset Load
GND_FLT | Int2 | Ground Fault |  | opc | ns=1;s=[{Device}]HR3292 | AtomicTag | WhenTrue | Alarm |  |  |  | Ground Fault | Normal¦Alarm | 0¦1
HIGH_AC_V | Int2 | High AC Voltage |  | opc | ns=1;s=[{Device}]HR400.3 | AtomicTag | WhenTrue | Alarm |  |  |  | High AC Voltage | Normal¦Alarm | 0¦1
HIGH_CLNT_TEMP | Int2 | High Coolant Temperature |  | opc | ns=1;s=[{Device}]HR400.7 | AtomicTag | WhenTrue | Alarm |  |  |  | High Coolant Temperature | Normal¦Alarm | 0¦1
HIGH_CLNT_TEMP_SHTDN | Int2 | High Coolant Temperature Shutdown |  | opc | ns=1;s=[{Device}]HR400.1 | AtomicTag | WhenTrue | Alarm |  |  |  | High Coolant Temperature Shutdown | Normal¦Alarm | 0¦1
I_3PH | Int2 | Three Phase Current | A | opc | ns=1;s=[{Device}]HR29 | AtomicTag | [5 empty] | Three Phase Current
I_A | Int2 | Current Phase A | A | opc | ns=1;s=[{Device}]HR26 | AtomicTag |  |  | TRUE | 5 | MIN | Current Phase A
I_B | Int2 | Current Phase B | A | opc | ns=1;s=[{Device}]HR27 | AtomicTag |  |  | TRUE | 5 | MIN | Current Phase B
I_C | Int2 | Current Phase C | A | opc | ns=1;s=[{Device}]HR28 | AtomicTag |  |  | TRUE | 5 | MIN | Current Phase C
I_N | Int2 | Neutral Current | A | opc | ns=1;s=[{Device}]HR30 | AtomicTag |  |  | TRUE | 5 | MIN | Neutral Current
KVA | Int2 | Apparent Power | kVA | opc | ns=1;s=[{Device}]HR43 | AtomicTag |  |  | TRUE | 5 | MIN | Apparent Power
KVAR | Int2 | Reactive Power | kVAR | opc | ns=1;s=[{Device}]HR38 | AtomicTag |  |  | TRUE | 5 | MIN | Reactive Power
KW | Int2 | Real Power | kW | opc | ns=1;s=[{Device}]HR34 | AtomicTag |  |  | TRUE | 5 | MIN | Real Power
LOW_AC_V | Int2 | Low AC Voltage |  | opc | ns=1;s=[{Device}]HR400.4 | AtomicTag | WhenTrue | Alarm |  |  |  | Low AC Voltage | Normal¦Alarm | 0¦1
LOW_BATT_V | Int2 | Low Battery Voltage |  | opc | ns=1;s=[{Device}]HR4.4 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Battery Voltage | Normal¦Alarm | 0¦1
LOW_CLNT_LVL | Int2 | Low Coolant Levels |  | opc | ns=1;s=[{Device}]HR3280 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Coolant Levels | Normal¦Alarm | 0¦1
LOW_CLNT_TEMP | Int2 | Low Coolant Temperature |  | opc | ns=1;s=[{Device}]HR400.8 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Coolant Temperature | Normal¦Alarm | 0¦1
LOW_FUEL_SW | Int2 | Low Fuel Switch |  | opc | ns=1;s=[{Device}]HR500 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Fuel Switch | Normal¦Alarm | 0¦1
LOW_OIL_PRES | Int2 | Low Oil Pressure |  | opc | ns=1;s=[{Device}]HR400.2 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Oil Pressure
NUM_STRT | Int4 | Number of Starts |  | opc | ns=1;s=[{Device}]HR75 | AtomicTag |  |  | TRUE | 5 | MIN | Number of Starts
OIL_PRES | Int2 | Oil Pressure | PSI | opc | ns=1;s=[{Device}]HR62 | AtomicTag | [5 empty] | Oil Pressure
OIL_TEMP | Int2 | Oil Temperature | °F | opc | ns=1;s=[{Device}]HR63 | AtomicTag | [5 empty] | Oil Temperature
OVR_FREQ | Int2 | Over Frequency |  | opc | ns=1;s=[{Device}]HR400.5 | AtomicTag | WhenTrue | Alarm |  |  |  | Over Frequency | Normal¦Alarm | 0¦1
OVRLD | Int2 | Overload |  | opc | ns=1;s=[{Device}]HR13.9 | AtomicTag | WhenTrue | Alarm |  |  |  | Overload | Normal¦Alarm | 0¦1
OVRSPD | Int2 | Overspeed |  | opc | ns=1;s=[{Device}]HR400.8 | AtomicTag | WhenTrue | Alarm |  |  |  | Overspeed | Normal¦Alarm | 0¦1
PF | Int1 | Power Factor |  | opc | ns=1;s=[{Device}]HR39 | AtomicTag | [5 empty] | Power Factor
PH_OVR_I | Int2 | Phase Over Current |  | opc | ns=1;s=[{Device}]HR8.1 | AtomicTag | WhenTrue | Alarm |  |  |  | Phase Over Current | Normal¦Alarm | 0¦1
REV_KW | Int4 | Reverse kW | kW | opc | ns=1;s=[{Device}]HR47 | AtomicTag | WhenTrue | Alarm |  |  |  | Reverse kW | Normal¦Alarm | 0¦1
TOT_FUEL | Int4 | Total Fuel Consumption | gal | opc | ns=1;s=[{Device}]HR73 | AtomicTag |  |  | TRUE | 5 | MIN | Total Fuel Consumption
TOT_KWH | Int4 | Total Kilowatt Hours |  | opc | ns=1;s=[{Device}]HR49 | AtomicTag | [5 empty] | Total Kilowatt Hours
UND_FREQ | Int2 | Under Frequency |  | opc | ns=1;s=[{Device}]HR400.6 | AtomicTag | WhenTrue | Alarm |  |  |  | Under Frequency | Normal¦Alarm | 0¦1
V_AB | Int2 | Voltage Phase A to Phase B | V | opc | ns=1;s=[{Device}]HR22 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Phase A to Phase B
V_AN | Int2 | Voltage Phase A to Neutral | V | opc | ns=1;s=[{Device}]HR18 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Phase A to Neutral
V_BC | Int2 | Voltage Phase B to Phase C | V | opc | ns=1;s=[{Device}]HR23 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Phase B to Phase C
V_BN | Int2 | Voltage Phase B to Neutral | V | opc | ns=1;s=[{Device}]HR19 | AtomicTag | [5 empty] | Voltage Phase B to Neutral
V_CA | Int2 | Voltage Phase C to Phase A | V | opc | ns=1;s=[{Device}]HR24 | AtomicTag | [5 empty] | Voltage Phase C to Phase A
V_CN | Int2 | Voltage Phase C to Nuetral | V | opc | ns=1;s=[{Device}]HR20 | AtomicTag | [5 empty] | Voltage Phase C to Nuetral
ENG_CTRL_WRN | Int2 | Engine Control Warning |  | opc | ns=1;s=[{Device}]HR228 | AtomicTag | WhenTrue | Alarm |  |  |  | Engine Control Warning | Normal¦Alarm | 0¦1
CTRL_MODE | Int2 | Controller Mode |  | opc | ns=1;s=[{Device}]HR283 | AtomicTag | [5 empty] | Controller Mode | Off¦Ready¦Setup¦Starting¦Idle¦Rated¦Stop Normal¦Stop Emergency¦Factory Test¦Wait to Power Down¦Regeneration | 0¦1¦2¦3¦4¦5¦6¦7¦8¦9¦10