## Sheet1
name | dataType | documentation | engUnit | valueSource | opcItemPath | tagType | alarmMode | alarmName | historyEnabled | historySampleRate | historySampleRateUnits | shortDescription | stateLabels | stateValues
ACCUM_BATT_TIME | Int2 | Accumulative Battery Time | hrs | opc | ns=1;s=[{Device}]IR191 | AtomicTag |  |  | TRUE | 5 | MIN | Accumulative Battery Time
AMB_OVR_TEMP | Boolean | Ambient Over Temperature |  | opc | ns=1;s=[{Device}]C283 | AtomicTag | WhenTrue | Alarm |  |  |  | Ambient Over Temperature | Normal¦Alarm | false¦true
BATT_AMP | Int2 | Battery Amps | A | opc | ns=1;s=[{Device}]IR201 | AtomicTag |  |  | TRUE | 5 | MIN | Battery Amps
BATT_CHRG_INHB | Boolean | Battery Charge Inhibit |  | opc | ns=1;s=[{Device}]C272 | AtomicTag | WhenTrue | Alarm |  |  |  | Battery Charge Inhibit | Normal¦Alarm | false¦true
BATT_CHRG_PCT | Int2 | Battery Charge Percent | % | opc | ns=1;s=[{Device}]IR188 | AtomicTag |  |  | TRUE | 5 | MIN | Battery Charge Percent
BATT_DISC_ALM | Boolean | Battery Disconnect Alarm |  | opc | ns=1;s=[{Device}]C273 | AtomicTag | WhenTrue | Alarm |  |  |  | Battery Disconnect Alarm | Normal¦Alarm | false¦true
BATT_IS | Int2 | Battery Is |  | opc | ns=1;s=[{Device}]IR193 | AtomicTag | [5 empty] | Battery Is | Fully Charged¦Charging¦Discharging¦Charger Off | 0¦1¦2¦3
BATT_STS | Int2 | Battery Status |  | opc | ns=1;s=[{Device}]IR192 | AtomicTag | WhenTrue | Alarm |  |  |  | Battery Status | Unknown¦Normal¦Low¦Depleted | 0¦1¦2¦3¦4
BATT_TEMP | Int2 | Battery Temperature | °C | opc | ns=1;s=[{Device}]IR187 | AtomicTag | [5 empty] | Battery Temperature
BATT_TIME_REM | Int2 | Battery Time Remaining | min | opc | ns=1;s=[{Device}]IR189 | AtomicTag | [5 empty] | Battery Time Remaining
BCB_STS | Int2 | Main Battery Circuit Breaker Status |  | opc | ns=1;s=[{Device}]IR181 | AtomicTag | [5 empty] | Main Battery Circuit Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
BFB_STS | Int2 | Bypass Isolation Breaker Status |  | opc | ns=1;s=[{Device}]IR36 | AtomicTag | [5 empty] | Bypass Isolation Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
BLO_FAN_FAIL | Boolean | Blower Fan Failure |  | opc | ns=1;s=[{Device}]C259 | AtomicTag | WhenTrue | Alarm |  |  |  | Blower Fan Failure | Normal¦Alarm | false¦true
BYP_NOT_AVBL | Boolean | Bypass Not Available |  | opc | ns=1;s=[{Device}]C25 | AtomicTag | WhenTrue | Alarm |  |  |  | Bypass Not Available | Normal¦Alarm | false¦true
CHGR_01_STS | Int2 | Charger 1 Status |  | opc | ns=1;s=[{Device}]IR134 | AtomicTag | [5 empty] | Charger 1 Status | Off¦On | 0¦1
CMN_ALM | Int2 | Common Alarm |  | opc | ns=1;s=[{Device}]IR169 | AtomicTag | WhenTrue | Alarm |  |  |  | Common Alarm | Normal¦Alarm | false¦true
CTRL_PWR_FAIL | Boolean | Control Power Failure |  | opc | ns=1;s=[{Device}]C17 | AtomicTag | WhenTrue | Alarm |  |  |  | Control Power Failure | Normal¦Alarm | false¦true
DC_BUS_ABN | Boolean | DC Bus Abnormal |  | opc | ns=1;s=[{Device}]C121 | AtomicTag | WhenTrue | Alarm |  |  |  | DC Bus Abnormal | Normal¦Alarm | false¦true
DC_BUS_FAIL | Boolean | DC Bus Failure |  | opc | ns=1;s=[{Device}]C122 | AtomicTag | WhenTrue | Alarm |  |  |  | DC Bus Failure | Normal¦Alarm | false¦true
DC_BUS_I | Int2 | DC Bus Current | A | opc | ns=1;s=[{Device}]IR185 | AtomicTag |  |  | TRUE | 5 | MIN | DC Bus Current
DC_BUS_V | Int2 | DC Bus Voltage | V | opc | ns=1;s=[{Device}]IR184 | AtomicTag |  |  | TRUE | 5 | MIN | DC Bus Voltage
DC_GND_FLT | Boolean | DC Ground Fault |  | opc | ns=1;s=[{Device}]C258 | AtomicTag | WhenTrue | Alarm |  |  |  | DC Ground Fault | Normal¦Alarm | false¦true
DSCHGR_01_STS | Int2 | Discharger 1 Status |  | opc | ns=1;s=[{Device}]IR144 | AtomicTag | [5 empty] | Discharger 1 Status | Off¦On | 0¦1
EMER_PWR_OFF | Boolean | Emergency Power Off |  | opc | ns=1;s=[{Device}]C256 | AtomicTag | WhenTrue | Alarm |  |  |  | Emergency Power Off | Normal¦Alarm | false¦true
EQUIP_OVR_TEMP | Boolean | Equipment Over Temperature |  | opc | ns=1;s=[{Device}]C252 | AtomicTag | WhenTrue | Alarm |  |  |  | Equipment Over Temperature | Normal¦Alarm | false¦true
I_IN_A | Int2 | Current In A | A | opc | ns=1;s=[{Device}]IR7 | AtomicTag |  |  | TRUE | 5 | MIN | Current In A
I_IN_B | Int2 | Current In B | A | opc | ns=1;s=[{Device}]IR8 | AtomicTag |  |  | TRUE | 5 | MIN | Current In B
I_IN_C | Int2 | Current In C | A | opc | ns=1;s=[{Device}]IR9 | AtomicTag |  |  | TRUE | 5 | MIN | Current In C
I_OUT_A | Int2 | Current Out A | A | opc | ns=1;s=[{Device}]IR44 | AtomicTag |  |  | TRUE | 5 | MIN | Current Out A
I_OUT_B | Int2 | Current Out B | A | opc | ns=1;s=[{Device}]IR45 | AtomicTag |  |  | TRUE | 5 | MIN | Current Out B
I_OUT_C | Int2 | Current Out C | A | opc | ns=1;s=[{Device}]IR46 | AtomicTag |  |  | TRUE | 5 | MIN | Current Out C
INP_FAIL | Boolean | Input Failure |  | opc | ns=1;s=[{Device}]C3 | AtomicTag | WhenTrue | Alarm |  |  |  | Input Failure | Normal¦Alarm | false¦true
INP_FREQ | Int2 | Input Frequency | Hz | opc | ns=1;s=[{Device}]IR10 | AtomicTag | [5 empty] | Input Frequency
INP_I_IMBAL | Boolean | Input Current Imbalance |  | opc | ns=1;s=[{Device}]C91 | AtomicTag | WhenTrue | Alarm |  |  |  | Input Current Imbalance | Normal¦Alarm | false¦true
INVRT_01_STS | Int2 | Inverter 1 Status |  | opc | ns=1;s=[{Device}]IR124 | AtomicTag | [5 empty] | Inverter 1 Status | Off¦On | 0¦1
INVRT_FLT | Boolean | Inverter Fault |  | opc | ns=1;s=[{Device}]C142 | AtomicTag | WhenTrue | Alarm |  |  |  | Inverter Fault | Normal¦Alarm | false¦true
INVRT_NOT_IN_SYNC | Boolean | Inverter Not In Sync |  | opc | ns=1;s=[{Device}]C144 | AtomicTag | WhenTrue | Alarm |  |  |  | Inverter Not In Sync | Normal¦Alarm | false¦true
LOW_BATT_ALM | Boolean | Low Battery Alarm |  | opc | ns=1;s=[{Device}]C277 | AtomicTag | WhenTrue | Alarm |  |  |  | Low Battery Alarm | Normal¦Alarm | false¦true
MBB_STS | Int2 | Maintenance Bypass Breaker Status |  | opc | ns=1;s=[{Device}]IR37 | AtomicTag | [5 empty] | Maintenance Bypass Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
MIB_STS | Int2 | Maintenance Isolation Breaker Status |  | opc | ns=1;s=[{Device}]IR69 | AtomicTag | [5 empty] | Maintenance Isolation Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
MODE | Int2 | Mode |  | opc | ns=1;s=[{Device}]IR166 | AtomicTag | [5 empty] | Mode
OUT_BKR_STS | Int2 | Module Output Breaker Status |  | opc | ns=1;s=[{Device}]IR68 | AtomicTag | [5 empty] | Module Output Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
OUT_FREQ | Int2 | Output Frequency | Hz | opc | ns=1;s=[{Device}]IR50 | AtomicTag | [5 empty] | Output Frequency
OUT_KVA | Int2 | Output kVA | kVA | opc | ns=1;s=[{Device}]IR61 | AtomicTag | [5 empty] | Output kVA
OUT_KW | Int2 | Output kW | kW | opc | ns=1;s=[{Device}]IR60 | AtomicTag | [5 empty] | Output kW
OVRLD_SHTDN | Boolean | Overload Shutdown |  | opc | ns=1;s=[{Device}]C143 | AtomicTag | WhenTrue | Alarm |  |  |  | Overload Shutdown | Normal¦Alarm | false¦true
PWR_OUT_OVRLD | Boolean | Power Output Overload |  | opc | ns=1;s=[{Device}]C13 | AtomicTag | WhenTrue | Alarm |  |  |  | Power Output Overload | Normal¦Alarm | false¦true
PWR_SYS_ON_GEN | Boolean | Power System on Generator |  | opc | ns=1;s=[{Device}]C254 | AtomicTag | WhenTrue | Alarm |  |  |  | Power System on Generator | Normal¦Alarm | false¦true
RECT_01_STS | Int2 | Rectifier 1 Status |  | opc | ns=1;s=[{Device}]IR94 | AtomicTag | [5 empty] | Rectifier 1 Status | Off¦On | 0¦1
RECT_FUSE_BLN | Boolean | Rectifier Fuse Blown |  | opc | ns=1;s=[{Device}]C257 | AtomicTag | [5 empty] | Rectifier Fuse Blown
REV_PWR | Boolean | Reverse Power |  | opc | ns=1;s=[{Device}]C5 | AtomicTag | WhenTrue | Alarm |  |  |  | Reverse Power | Normal¦Alarm | false¦true
RIB_STS | Int2 | Rectifier Isolation Breaker Status |  | opc | ns=1;s=[{Device}]IR22 | AtomicTag | [5 empty] | Rectifier Isolation Breaker Status | Open¦Closed¦Not Installed | 0¦1¦2
STATIC_BYP_SW_STS | Int2 | Static Bypass Switch Status |  | opc | ns=1;s=[{Device}]IR73 | AtomicTag | [5 empty] | Static Bypass Switch Status | Off¦On | 0¦1
STATIC_BYP_V_AB | Int2 | Static Bypass Voltage A-B | V | opc | ns=1;s=[{Device}]IR23 | AtomicTag | [5 empty] | Static Bypass Voltage A-B
STATIC_BYP_V_BC | Int2 | Static Bypass Voltage B-C | V | opc | ns=1;s=[{Device}]IR24 | AtomicTag | [5 empty] | Static Bypass Voltage B-C
STATIC_BYP_V_CA | Int2 | Static Bypass Voltage C-A | V | opc | ns=1;s=[{Device}]IR25 | AtomicTag | [5 empty] | Static Bypass Voltage C-A
SYS_OUT_PCT_A | Int2 | System Output Percent Phase A | % | opc | ns=1;s=[{Device}]IR65 | AtomicTag | [5 empty] | System Output Percent Phase A
SYS_OUT_PCT_B | Int2 | System Output Percent Phase B | % | opc | ns=1;s=[{Device}]IR66 | AtomicTag | [5 empty] | System Output Percent Phase B
SYS_OUT_PCT_C | Int2 | System Output Percent Phase C | % | opc | ns=1;s=[{Device}]IR67 | AtomicTag | [5 empty] | System Output Percent Phase C
TOT_BATT_DSCHRG | Int2 | Total Battery Discharge |  | opc | ns=1;s=[{Device}]IR190 | AtomicTag | [5 empty] | Total Battery Discharge
TOT_OPRG_HRS | Int2 | Total Operating Hours | hrs | opc | ns=1;s=[{Device}]IR164 | AtomicTag | [5 empty] | Total Operating Hours
UPS_ON_BYP | Boolean | UPS on Bypsass |  | opc | ns=1;s=[{Device}]C266 | AtomicTag | WhenTrue | Alarm |  |  |  | UPS on Bypsass | Normal¦Alarm | false¦true
UPS_ONLINE | Int2 | UPS Online |  | opc | ns=1;s=[{Device}]IR167 | AtomicTag | [5 empty] | UPS Online
V_IN_AB | Int2 | Voltage In A-B | V | opc | ns=1;s=[{Device}]IR1 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage In A-B
V_IN_BC | Int2 | Voltage In B-C | V | opc | ns=1;s=[{Device}]IR2 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage In B-C
V_IN_CA | Int2 | Voltage In C-A | V | opc | ns=1;s=[{Device}]IR3 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage In C-A
V_OUT_AB | Int2 | Voltage Out A-B | V | opc | ns=1;s=[{Device}]IR38 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out A-B
V_OUT_AN | Int2 | Voltage Out A-N | V | opc | ns=1;s=[{Device}]IR41 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out A-N
V_OUT_BC | Int2 | Voltage Out B-C | V | opc | ns=1;s=[{Device}]IR39 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out B-C
V_OUT_BN | Int2 | Voltage Out B-N | V | opc | ns=1;s=[{Device}]IR42 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out B-N
V_OUT_CA | Int2 | Voltage Out C-A | V | opc | ns=1;s=[{Device}]IR40 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out C-A
V_OUT_CN | Int2 | Voltage Out C-N | V | opc | ns=1;s=[{Device}]IR43 | AtomicTag |  |  | TRUE | 5 | MIN | Voltage Out C-N
WRN_SMRY_ALM | Int2 | Warning Summary Alarm |  | opc | ns=1;s=[{Device}]IR169 | AtomicTag | WhenTrue | Alarm |  |  |  | Warning Summary Alarm | Normal¦Alarm | false¦true