## Instructions
Ignition UDT Definition Builder
How to use this workbook:
1. Fill out the 'UDT' sheet: the UDT name, optional parent type, and any UDT Parameters (e.g. Device).
2. Fill out the 'Tags' sheet: one row per member tag. Cells with a dropdown arrow are validated.
3. (Optional) Fill out the 'Alarms' sheet: one row per alarm. 'tagName' must match a name on 'Tags'.
4. (Optional) Fill out the 'States' sheet: one row per state. 'tagName' must match a name on 'Tags'.
5. Save, then run: python ignition_udt_tool.py build <thisfile>.xlsx output.json
6. In Ignition: Tag Browser > Import icon > select output.json.
Notes:
- Every tag ALWAYS gets a 'Metadata' custom property with shortDescription + longDescription.
Add states for a tag on the 'States' sheet and they land under Metadata.states.
- Only 'name' is required per tag row. Leave any field blank to use the Ignition default.
- The 'Lists' sheet holds all allowable values. You may extend 'historyProvider' and 'tagGroup' there.
- Reference UDT parameters in OPC paths with braces, e.g. ns=1;s=[{Device}]
- 'valueSource' uses the JSON value 'db' for a SQL Query tag (the editor labels it 'Query').

## Lists
dataType | valueSource | tagType | sampleMode | historicalDeadbandStyle | sampleRateUnits | deadbandMode | alarmMode | priority | boolean | parameterType | historyProvider* | tagGroup*
Boolean | opc | AtomicTag | OnChange | Auto | MS | Absolute | Equality | Diagnostic | TRUE | String
Int1 | memory | Folder | Periodic | Analog_Compressed | SEC | Percent | AboveValue | Low | FALSE | Integer | Historian | default
Int2 | expr | UdtType | TagGroup | Discrete | MIN | Off | BelowValue | Medium |  | Float | Sensor_Data | Default Historical
Int4 | db | UdtInstance |  |  | HOUR |  | BetweenValues | High |  | Boolean | Edge Historian | OneSecond
Int8 | reference |  |  |  | DAY |  | OutsideValues | Critical |  |  |  | OneMinute
Float4 | derived |  |  |  | WEEK |  | OutOfRange
Float8 |  |  |  |  | MONTH |  | AnyChange
String |  |  |  |  | YEAR |  | BadQuality
DateTime | [6 empty] | OnCondition
BooleanArray
Int1Array
Int2Array
Int4Array
Int8Array
Float4Array
Float8Array
StringArray
DateTimeArray
DataSet
ByteArray
Document

## UDT
UDT Definition
UDT Name | STD_DI_2 | REQUIRED. e.g. STD_DI
Parent Type (typeId) |  | Optional. Name/path of a parent UDT to inherit from.
Default Tag Group |  | Optional. Applied to members that leave tagGroup blank.
UDT Parameters
Parameter Name | Type | Value
Device | String
Server | String | Ignition OPC UA Server
Note on A8: e.g. Device
Note on B8: String ¦ Integer ¦ Float ¦ Boolean
Note on C8: Default value for this parameter

## Tags
name | tagType | dataType | valueSource | opcItemPath | opcServer | expression | documentation | tooltip | shortDescription | longDescription | engUnit | engLow | engHigh | formatString | tagGroup | deadband | deadbandMode | historyEnabled | historyProvider | sampleMode | historySampleRate | historySampleRateUnits | historicalDeadband | historicalDeadbandStyle | historicalDeadbandMode
EnableIn | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Enable Input - System Defined Parameter |  | Enable Input | [8 empty] | FALSE
EnableOut | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Enable Output - System Defined Parameter |  | Enable Output | [8 empty] | FALSE
Inp_PVraw | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Physical digital input signal (raw state before inversion, debounce, or simulation). |  | Raw Input | [8 empty] | FALSE
Sts_AlarmActv | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Status bit indicating any alarm associated with this digital input is currently active. |  | Alarm Active Status | [8 empty] | FALSE
Wrk_PVActv | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Internal active state after inversion and debounce; 1 = input logically energized. | [10 empty] | FALSE
Actv_RawInputState | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Raw input status (after sim selection) before inversion and debounce; 1 = input energized. | [10 empty] | FALSE
Sts_ResetReady | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Status indicating all alarm conditions are cleared and the operator may issue a reset. | [10 empty] | FALSE
Cfg_DB_TIME | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Debounce time in milliseconds applied to the digital input On/Off transitions. |  | Debounce Time | [8 empty] | FALSE
Cfg_Invert_Enable | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | When true, logically invert the raw input state before debounce and alarm evaluation. |  | Invert Raw Input | [8 empty] | FALSE
Cmd_Reset | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Local reset command for alarms associated with this digital input. |  | Alarm Reset Command | [8 empty] | FALSE
Inp_SimRawState | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Simulated raw input state used when raw simulation mode is active. | [10 empty] | FALSE
Cfg_TargetState | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Global executive device control structure for this digital input (HOA, alarms, and system coordination). | [10 empty] | FALSE
Cfg_SystemNumber | AtomicTag | Int2 | opc | ns=1;s=[{Device}] | {Server} |  | Target (expected) logical state of the input used for target deviation alarm checking. | [10 empty] | FALSE
Enable_SimRaw | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | System index into global Exec.SysCtrl array for this digital input's alarms and status. |  | Enable Raw Simulation | [8 empty] | FALSE
Enable_SimEU | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Local enable for raw simulation mode (sets EnumSimMode to raw simulation). |  | Enable EU Simulation | [8 empty] | FALSE
Sts_SimRawSig | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Local enable for EU-level simulation mode (sets EnumSimMode to EU simulation). |  | Raw Simulation Status | [8 empty] | FALSE
Sts_SimEU | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Status indicating raw simulation mode is currently selected. |  | EU Simulation Status | [8 empty] | FALSE
Out_PVActv | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Status indicating EU-level simulation mode is currently selected. | [10 empty] | TRUE | History | OnChange
Inp_SimEUState | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Final active process value (PV) after simulation, inversion, and debounce; 1 = input ON. | [10 empty] | FALSE
Inp_IOFault | AtomicTag | Boolean | opc | ns=1;s=[{Device}] | {Server} |  | Simulated logical PV state used when EU simulation mode is active. |  | IO Fault | [8 empty] | FALSE
Cfg_IOFault_Type | AtomicTag | Int2 | opc | ns=1;s=[{Device}] | {Server} |  | External I/O fault input (card fault, open-wire, etc.) for this digital input. | [10 empty] | FALSE
Note on A1: REQUIRED. Member tag / parameter name (e.g. Inp_PVraw).
Note on B1: AtomicTag (default), Folder, UdtInstance, UdtType.
Note on C1: Ignition data type. Dropdown.
Note on D1: opc ¦ memory ¦ expr ¦ db ¦ reference ¦ derived. Dropdown.
Note on E1: OPC address, e.g. ns=1;s=[{Device}] (only for valueSource=opc).
Note on F1: OPC server name (only for valueSource=opc). Blank uses default.
Note on G1: Expression text (only for valueSource=expr).
Note on H1: Built-in Ignition documentation field.
Note on I1: Short hover tooltip.
Note on J1: Metadata custom property -> Metadata.shortDescription (always emitted).
Note on K1: Metadata custom property -> Metadata.longDescription (always emitted).
Note on L1: Engineering unit, e.g. V, A, Hz, degF.
Note on M1: Engineering range low (numeric).
Note on N1: Engineering range high (numeric).
Note on O1: Display format, e.g. #,##0.##
Note on P1: Tag group / scan class. Editable dropdown.
Note on Q1: Value deadband (numeric).
Note on R1: Absolute ¦ Percent ¦ Off. Dropdown.
Note on S1: TRUE/FALSE. Turns on tag historian for this tag.
Note on T1: Tag Historian provider name. Editable dropdown.
Note on U1: OnChange ¦ Periodic ¦ TagGroup. Dropdown.
Note on V1: History sample rate (numeric, used when sampleMode=Periodic).
Note on W1: MS ¦ SEC ¦ MIN ¦ HOUR ¦ DAY ¦ WEEK ¦ MONTH ¦ YEAR. Dropdown.
Note on X1: Historical deadband (numeric).
Note on Y1: Auto ¦ Analog_Compressed ¦ Discrete. Dropdown.
Note on Z1: Absolute ¦ Percent ¦ Off. Dropdown.

## Alarms
tagName | alarmName | mode | setpointA | setpointB | priority | enabled | timeOnDelaySeconds | timeOffDelaySeconds | displayPath
Sts_AlarmActv | Active Alarm | whenTrue |  |  | High | TRUE
Note on A1: REQUIRED. Must match a name on the Tags sheet.
Note on B1: REQUIRED. Alarm label, e.g. 'High Alarm'.
Note on C1: Alarm condition. Dropdown.
Note on D1: Primary setpoint (numeric). For Boolean Equality use 1 or 0.
Note on E1: Second setpoint (only for BetweenValues/OutsideValues).
Note on F1: Diagnostic ¦ Low ¦ Medium ¦ High ¦ Critical. Dropdown.
Note on G1: TRUE/FALSE. Dropdown.
Note on H1: Delay before the alarm becomes active (numeric).
Note on I1: Delay before the alarm clears (numeric).
Note on J1: Optional friendly path shown in alarm displays.

## States
tagName | label | value
Note on A1: REQUIRED. Must match a name on the Tags sheet.
Note on B1: State label, e.g. Normal / Alarm / Running / Stopped.
Note on C1: State value: TRUE/FALSE, an integer (0,1,2...), or text. Type auto-detected.